## Slide 1: ROMEO H2020 Project
Digital Twins in offshore wind
Wind Energy Science Conference
18th June 2019
University College Cork, Ireland
Photo: Iberdrola
Notes: In short: Digital twins are a virtual representation of the elements and dynamics of an asset throughout its entire lifecycle
I want to show the application of this concept to an offshore wind farm, namely Wikinger in the Baltic Sea operated by Iberdrola

## Slide 2: Where Do digital Twins come from?
APOLLO 13 MISSION
NASA
FIRST IMPLEMENTATION AT OFFSHORE PLATFORM
Ramboll established first Digital Twin for Lifetime Extension
1970
2002
2006
2017
Similar challenge faced in different industries:
Remote asset to be maintained and operated over entire lifetime, whereas the physical access is difficult.
DITGITAL TWIN TERMINOLOGY
Michael Grieves, U of Michigan
ROMEO PILOT PROJECT
Ramboll established first Digital Twin of an offshore wind jacket
Notes: Before we go into detail just a short history excursion to where digital twins came from
It started out already nearly 50 years ago when a physical copy of the Apollo 13 spacecraft on the earth helped the crew deal with the challenging situation in space. The copy helped to suggest the best possible steps to fix the problems.
It took some time until the digital twin terminology was established in 2002
In 2006 Ramboll first introduced the digital twin concept to an offshore platform and achieved a considerable life time extension of the platform
This concept from oil & gas is now transferred to the field of offshore wind within the ROMEO project
All in all many industries face the similar challenge of remotely maintaining an asset over the entire lifetime without physically accessing it.

## Slide 3: Motivation of Digital twins
Measurements show deviations in structural dynamics between installed WTG and their corresponding FE model
Design process & assumptions are governed by certification standards
Timeline of projects does not allow for thorough site investigations
  conservative design decisions for the foundation structure are taken
Measurement data justifies to deviate from common practice
Notes: So what are the motivation of a digital twin in offshore wind?
There is a deviation between the installed WTG and the corresponding FE model from design
This is often due the design process which is governed by certification standards
Also the timeline of projects sometimes does not allow for thorough site investigations
We nearly always end up with a model that does not reflect the reality and the measurement data justifies to establish a digital twin

## Slide 4: AGENDA - Digital Twin roadmap
01
Optimal sensor placement
Cost effective and purpose specific sensor layout
02
FE Model Updating
Updated model parameter
Structural behaviour as installed
04
Reduction of uncertainties
Extended fatigue life
Reduced inspection costs
05
Damage detection
Evaluation of real time data
Warnings based on trends and predictions
03
Wave & wind load calibration
Updated wave load coefficients
Notes: The digital twin is established in several steps:
Sensors are needed to obtain the as-installed state of the wind turbine in the real world
With the measurements received from the sensors the finite element model can be updated to reflect the reality in terms of dynamical behaviour
The loads applied to the structure, mainly wind and waves, can be measured and refine the loads in the finite element model
These updating steps lead to less uncertainties in the model and generally extend the calculated lifetime of the asset
Through the continuous data stream from the sensors also damage detection is possible

## Slide 5: Dynamics of Wikinger WTG
1st bending |  | 1st torsional | 2nd bending | 
fore-aft | side-side |  | fore-aft | side-side
Notes: To understand how the accelerometers are placed we need to check how the finite element model behaves dynamically
Here the first five analytical harmonics of a jacket structure are shown which the sensor setup should be able to capture

## Slide 6: 01 Optimal sensor placement – ROMEO Project
Optimal placement is defined by:
  Minimum amount of hardware
  Best accessible locations
  Accurate observability of mode shapes dependent on chosen level of detectability (monitoring strategy)
Support structure and wind farm location specific sensor placement
Ensures best value of CMS for at least 25 years of operation
accelerometers
Modal assurance criterion
(MAC-matrix)
WIKINGER
WTG
Notes: The goal is to find the minimum amount of hardware and place them at the best accessible locations while extracting the mode shapes specified beforehand
Based on Monitoring Strategy, accelerometers can be placed to exactly meet the demands for the digital twin
In this example the Wikinger WTG is equipped with 5 accelerometers to extract the first 5 harmonics of the structure
Sensors are located on the transition piece and the tower top
As the digital twin concept accompanies the structure during the entire lifecycle the sensors need to operate for at least 25 years

## Slide 7: 02 FE Model update
Goal:
  Update modal parameters of the FE model so that it better represents the installed structure
Updating process:
  FE model parameter selection
  Sensitivity analysis on parameters
  Bayesian updating of parameters
    weighting coefficients
    realistic boundaries
FE model
Measurement model
Notes: The goal is to update the FE model in such a way that it matches with the measurement data
Model parameter are chosen based on engineering judgement, a sensitivity analysis is performed to see the influence on the modal parameter
Then the parameters are changed based on the sensitivity, weighing coefficients and set boundaries.
In the example on the right a harmonic of the FE model is shown with respect to the extracted mode of the accelerometers. After the model update both models should match

## Slide 8: 03 Wave Load Calibration
Identification of real loads
  Access to entire load history
Update of the FE model loads based on measurement data
  3 wave radars needed to capture the directional sea state
Recalculation of ULS and FLS
Wave Radar REX
Photo: RS Aqua. Copyright 2019
Notes: In a second updating stage the real loads applied to the structure are updated based on measurement data.
The design comprises loads derived from statistics whereas in a digital twin the real loads are known.
Usually wave radars or wave buoys are used to capture the directional sea state
Recalculation of ultimate loads and fatigue loads is possible.

## Slide 9: 04 Extended fatigue life
Recalculation of fatigue limit state (FLS) using:
  Modally updated FE model
  Load updated FE model
Shifting of fatigue hot spots
Extension of fatigue life
Notes: As a result the fatigue at governing hot spots is usually reduced
In the diagram this is shown by the orange and grey bars, over all hotspot groups the fatigue damage is reduced or shifted
This means lifetime extension of the structure can be realised

## Slide 10: 05 Damage Detection
Continuous monitoring through real time data analysis algorithm
  Confidence in known structural behaviour allows for modal tracking of healthy structure
  Deviation in mode shape & natural frequency from the virgin model indicates change of the system -> damage
  Type of deviation leads to damage localisation
  Predictive warnings based on patterns and trends
FE model
Measurement model
Notes: Digital twins are also used for damage detection purposes
A virgin model is established right after installation which represent the undamaged case
Any deviation in mode shape & natural frequency then indicates that the system has changed
The type of change leads to the damage identification and localisation
This is done with a continuous data stream that is analysed in the cloud

## Slide 11: 05 Damage detection Example: Scour
Natural frequency
Mode shape
Virgin model of healthy structure can be tested for anticipated damages
Localisation of damages possible
Notes: Example for the lookup table for scour is shown in this slide
For scour detection the natural frequency and mode shapes change when the global scour depth increases as shown in the diagrams. The coloured lines correspond to mode 1-5.
This is change is picked up by our acceleration sensors and we can detect a change in the global dynamics
There is a lookup table with natural frequency and mode shape for each possible damage (from FE model), eg. Member failure, grout connection, etc.

## Slide 12: summary
A digital twin is a model that represents the behaviour of the structure as-installed
It gives access to the structural behaviour of the entire lifecycle
Leading to:
  Lifetime extension of existing wind farms through updated fatigue calculation
  Exact planning of O&M activities through continuous monitoring algorithms
  Optimisation of new foundation designs, e.g. inclusion of more realistic soil profile through the transfer of findings
Notes: To conclude: A digital twin is a model that better represents the behaviour of the installed structure compared to the FE model
This leads to optimisation of new foundation designs
Lifetime extension of existing wind farms
Better O&M strategies

## Slide 13: Thanks for your attention!
Contact
Simon Siedler – Project Engineer Ramboll Offshore Wind
simon.siedler@ramboll.com
Ursula Smolka – Chief Consultant Ramboll Offshore Wind
ursula.smolka@ramboll.com
Tim Fischer – Vice Director Ramboll Wind
tim.fischer@ramboll.com
www.ramboll.com/wind